## Page1_Table1
ITEM DESCRIPTION | PART NO. | QTY | MATERIAL | SPECIFICATION | FABRICATION | REMARKS
PAD | SAQ4D-2X16 | 2 |  | PLATE - 6mm Thk
LIFTING LUG | SAQ4D-2X4 | 2 |  | PLATE - 12mm Thk
LIFTING LUG | SAQ4D-2X4 | 2 |  | PLATE - 12mm Thk
PAD | SAQ4D-2X16 | 2 |  | PLATE - 6mm Thk
PAD | SAQ4D-2X16 | 2 |  | PLATE - 6mm Thk
INS. | SAQ4D-2X4 | 2 |  | PLATE - 6mm Thk
INS. | SAQ4D-2X4 | 2 |  | PLATE - 6mm Thk
BASE PLATE | SAQ4D-10X6 | 1

## Page1_Table2
NOZZLE | QTY | SIZE | SUPPORT | ORIENTATION | FLANGE MATERIAL | TYPE OF FLANGE/FITTING | SERVICE
N1 | 1 | 2"NPSM | SCH-40/40S | SA182 F316 | ASME B16.5, CL150, SORF | VENT/DRN, C/B BLK
N2 | 1 | 2"NPSM | SCH-40/40S | SA182 F316 | ASME B16.5, CL150, SORF | VENT/DRN, C/B BLK
N3 | 1 | DN50 | SCH-40/40S | SA182 F316 | ASME B16.5, CL150, SORF | CHILLED WATER INLET
N4 | 1 | DN50 | SCH-40/40S | SA182 F316 | ASME B16.5, CL150, SORF | CHILLED WATER OUTLET
N5 | 1 | 2"NPSM | SCH-40/40S | SA182 F316 | ASME B16.5, CL150, SORF | VENT/DRN, C/B BLK
N6 | 1 | 2"NPSM | SCH-40/40S | SA182 F316 | ASME B16.5, CL150, SORF | VENT/DRN, C/B BLK
N7 | 1 | 2"NPSM | SCH-40/40S | SA182 F316 | ASME B16.5, CL150, SORF | WATER DMDG INLET
N8 | 1 | 2"NPSM | SCH-40/40S | SA182 F316 | ASME B16.5, CL150, SORF | WATER DMDG OUTLET

## Page1_Table3
DESIGN CODE | SHELL SIDE | TUBE SIDE
DESIGN | PRESSURE : 10 Barg | 60
TEST | HYDROSTATIC : 15.0barg | 10.40
FITTING | PREHEAT : 0.70 barg | 0.70
JOINT | L : 0.70 | 0.70
EFFICIENCY | E : 0.70 | 0.70
CORROSION ALLOWANCE | CA : 0.70 | 0.70

## Page1_Table4
ITEM | VALUE
DESIGN TEMPERATURE | C : 60
WORKING FLUID | CHILLED WATER
BIOCIDIDE DOSAGE | NL
LIQUID FOULING FACTANT DOSAGE | NL
POST WELD HEAT TREATMENT | DEMOUNTED PER UHA-32
IMPACT TEST | DEMOUNTED PER UHA-51(0)
MWP | BAR : 0
MDL | KG : 0
REFLUID | CALCULATED : 24hrs (BY OTHERS)
SPARIAL | 3.3
PREPARATION | PT : NL
ROTTING SURFACE AREA | MD : NL
VALUE | 0.130
EMPTY WEIGHT | KG : 530
FULL WATER WEIGHT | KG : 913
L.THA. SERVICE | N2

## Page2_Table1
ITEM | DESCRIPTION | MATERIAL | QUANTITY | UNIT | REMARKS
1 | HDG | SA403-316 | 2 |  | INC. GASKET-3M3300 SC# 105
2 | SHELL | SA516-70N19 | 2 |  | PTFE-LINED S/N 102
3 | PARTITION PLATE | SA516-70N19 | 2 |  | PLATE-BEAM THK
4 | BEND TUBES | SA213-316L | 18 |  | LASER-CUT ARC SECT. BENDS C/S 18.5 CLSS STD
5 | TUBESHEET | SA516-70N19 | 2 |  | PTFE-LINED THK
6 | LOWER BAFFLE | SA516-70N19 | 2 |  | PTFE-LINED THK
7 | SPACER TUBE | SA213-316L | 19 |  | PTFE-LINED SC# 125.155
8 | TE ROD | SS316 | 6
9 | HDG NUT | SS316 | 8 |  | NUT- HEX-M8
10 | WASHER | SS316 | 4 |  | FLAT WASHER-M8
11 | STUD BOLT | B18.3-1938 | 12 |  | STUD BOLT 5/8"-11 x 185mm(L)
12 | JACK BOLT | A193-B7 | 4
13 | FLAT WASHER | A194-2H | 24 |  | FLAT WASHER-M8 THK
14 | PIPE | SA312-316L | 2
15 | TUBE | SA213-TP316L | 14 |  | TUBE-TP316L 20mm x 2.0mm THK
16 | GASKET | NON-ASBESTOS | 2 |  | GASKET-3M3300 THK

## All_Tables
ITEM DESCRIPTION | PART NO. | QTY | MATERIAL | SPECIFICATION | FABRICATION | REMARKS | NOZZLE | SIZE | SUPPORT | ORIENTATION | FLANGE MATERIAL | TYPE OF FLANGE/FITTING | SERVICE | DESIGN CODE | SHELL SIDE | TUBE SIDE | ITEM | VALUE | DESCRIPTION | QUANTITY | UNIT
PAD | SAQ4D-2X16 | 2 |  | PLATE - 6mm Thk
LIFTING LUG | SAQ4D-2X4 | 2 |  | PLATE - 12mm Thk
LIFTING LUG | SAQ4D-2X4 | 2 |  | PLATE - 12mm Thk
PAD | SAQ4D-2X16 | 2 |  | PLATE - 6mm Thk
PAD | SAQ4D-2X16 | 2 |  | PLATE - 6mm Thk
INS. | SAQ4D-2X4 | 2 |  | PLATE - 6mm Thk
INS. | SAQ4D-2X4 | 2 |  | PLATE - 6mm Thk
BASE PLATE | SAQ4D-10X6 | 1
--- Page 1, Table 2 ---
|  | 1 |  |  |  |  | N1 | 2"NPSM | SCH-40/40S | SA182 F316 | ASME B16.5, CL150, SORF | VENT/DRN, C/B BLK
|  | 1 |  |  |  |  | N2 | 2"NPSM | SCH-40/40S | SA182 F316 | ASME B16.5, CL150, SORF | VENT/DRN, C/B BLK
|  | 1 |  |  |  |  | N3 | DN50 | SCH-40/40S | SA182 F316 | ASME B16.5, CL150, SORF | CHILLED WATER INLET
|  | 1 |  |  |  |  | N4 | DN50 | SCH-40/40S | SA182 F316 | ASME B16.5, CL150, SORF | CHILLED WATER OUTLET
|  | 1 |  |  |  |  | N5 | 2"NPSM | SCH-40/40S | SA182 F316 | ASME B16.5, CL150, SORF | VENT/DRN, C/B BLK
|  | 1 |  |  |  |  | N6 | 2"NPSM | SCH-40/40S | SA182 F316 | ASME B16.5, CL150, SORF | VENT/DRN, C/B BLK
|  | 1 |  |  |  |  | N7 | 2"NPSM | SCH-40/40S | SA182 F316 | ASME B16.5, CL150, SORF | WATER DMDG INLET
|  | 1 |  |  |  |  | N8 | 2"NPSM | SCH-40/40S | SA182 F316 | ASME B16.5, CL150, SORF | WATER DMDG OUTLET
--- Page 1, Table 3 ---
[14 empty] | DESIGN | PRESSURE : 10 Barg | 60
[14 empty] | TEST | HYDROSTATIC : 15.0barg | 10.40
[14 empty] | FITTING | PREHEAT : 0.70 barg | 0.70
[14 empty] | JOINT | L : 0.70 | 0.70
[14 empty] | EFFICIENCY | E : 0.70 | 0.70
[14 empty] | CORROSION ALLOWANCE | CA : 0.70 | 0.70
--- Page 1, Table 4 ---
[17 empty] | DESIGN TEMPERATURE | C : 60
[17 empty] | WORKING FLUID | CHILLED WATER
[17 empty] | BIOCIDIDE DOSAGE | NL
[17 empty] | LIQUID FOULING FACTANT DOSAGE | NL
[17 empty] | POST WELD HEAT TREATMENT | DEMOUNTED PER UHA-32
[17 empty] | IMPACT TEST | DEMOUNTED PER UHA-51(0)
[17 empty] | MWP | BAR : 0
[17 empty] | MDL | KG : 0
[17 empty] | REFLUID | CALCULATED : 24hrs (BY OTHERS)
[17 empty] | SPARIAL | 3.3
[17 empty] | PREPARATION | PT : NL
[17 empty] | ROTTING SURFACE AREA | MD : NL
[17 empty] | VALUE | 0.130
[17 empty] | EMPTY WEIGHT | KG : 530
[17 empty] | FULL WATER WEIGHT | KG : 913
[17 empty] | L.THA. SERVICE | N2
--- Page 2, Table 5 ---
|  |  | SA403-316 |  |  | INC. GASKET-3M3300 SC# 105 | [10 empty] | 1 |  | HDG | 2
|  |  | SA516-70N19 |  |  | PTFE-LINED S/N 102 | [10 empty] | 2 |  | SHELL | 2
|  |  | SA516-70N19 |  |  | PLATE-BEAM THK | [10 empty] | 3 |  | PARTITION PLATE | 2
|  |  | SA213-316L |  |  | LASER-CUT ARC SECT. BENDS C/S 18.5 CLSS STD | [10 empty] | 4 |  | BEND TUBES | 18
|  |  | SA516-70N19 |  |  | PTFE-LINED THK | [10 empty] | 5 |  | TUBESHEET | 2
|  |  | SA516-70N19 |  |  | PTFE-LINED THK | [10 empty] | 6 |  | LOWER BAFFLE | 2
|  |  | SA213-316L |  |  | PTFE-LINED SC# 125.155 | [10 empty] | 7 |  | SPACER TUBE | 19
|  |  | SS316 | [13 empty] | 8 |  | TE ROD | 6
|  |  | SS316 |  |  | NUT- HEX-M8 | [10 empty] | 9 |  | HDG NUT | 8
|  |  | SS316 |  |  | FLAT WASHER-M8 | [10 empty] | 10 |  | WASHER | 4
|  |  | B18.3-1938 |  |  | STUD BOLT 5/8"-11 x 185mm(L) | [10 empty] | 11 |  | STUD BOLT | 12
|  |  | A193-B7 | [13 empty] | 12 |  | JACK BOLT | 4
|  |  | A194-2H |  |  | FLAT WASHER-M8 THK | [10 empty] | 13 |  | FLAT WASHER | 24
|  |  | SA312-316L | [13 empty] | 14 |  | PIPE | 2
|  |  | SA213-TP316L |  |  | TUBE-TP316L 20mm x 2.0mm THK | [10 empty] | 15 |  | TUBE | 14
|  |  | NON-ASBESTOS |  |  | GASKET-3M3300 THK | [10 empty] | 16 |  | GASKET | 2